## Sheet1
Name of Company | Tiara infrastructure Limited
Name of work | Piling & Road Work
Location of Work | NAME OF WORK: PILING AND CIVIL WORKS FOR AVU AND DCU REVAMP, NEW HGU AND OFFSITE UTILITIES FOR DR 1.0 EXPANSION PROJECT OF INDIAN OIL CORPORATION LIMITED, DIGBOI REFINERY, ASSAM
Name Of Contractor
Adress
GST Number
Email ID

## Table 9
PRICE SCHEDULE FOR PILING AND CIVIL WORKS FOR AVU AND DCU REVAMP, NEW HGU AND OFFSITE FACILITIES FOR DR 1.0 EXPANSION PROJECT AT DIGBOI REFINERY OF INDIAN OIL CORPORATION LIMITED
| SCHEDULES OF RATES - PILING WORKS TENDER REF. NO:TP/214227C001/T/06 |  |  | SP1- PART A
S.NO. | DESCRIPTION OF ACTIVITIES | UNIT | QUANTITY | UNIT RATE (INR) | TOTAL AMOUNT (INR)
1 | BORED CAST-IN-SITU PILING
Construction of Bored Cast In Situ RCC Piles Execution of pile bore by rotary and/or percussion means in all kind of soil including hard murrum / WBM if any, including the use of bentonite mud, if required, supply, casting and vibration of concrete, including concrete quality control tests and disposal of the excavated earth/ muck/other materials inside/outside refinery premises up to a lead of 6 KM as advised by EIC. The disposal of muck produced during piling operations shall be in the scope of contractor without any additional charge, issue of driving records including shifting plant and equipments from one pile location to another in different areas of plant. The contractor shall get the concrete Design Mix approved by EIC. The rates shall also include the cost of approved admixture if any as per Design Mix. Concreting of piles to be done minimum 0.60 M above cut-off levels complete as per drawing, specification and directions of Engineer-in-charge for the following diameter & length of piles
1.1 | Diameter of pile-450 MM, length of pile-18M (Approx.), Grade of Concrete-M30, with minimum cement content as per IS:456 and relevant IS code ( Note:-Length of pile shall be measured from tip to cutoff elevation of piles. Reinforcement shall be measured and paid separately.) | Metre | 10620
1.2 | Diameter of pile-600 MM, length of pile-18M (Approx.), Grade of Concrete-M30, with minimum cement content as per IS:456 and relevant IS code( Note:-Length of pile shall be measured from tip to cutoff elevation of piles. Reinforcement shal be measured and paid separately.) | Metre | 4680
2 | STEEL REINFORCEMENT
| Supplying and fixing in position TMT bars reinforce- ment of grade Fe500/500D conforming to IS:1786, (Latest Version) for RCC Bored Cast-in-Situ piles for full length of pile including cost of steel and cost of binding wire, carting the same to site of work, straightening, cleaning, cutting, binding with 18 SWG black soft annealed binding wire, and placing with proper cover blocks, supports, chairs, spacers, welding if required to form a rigid cage complete for all heights and depths complete as per drawing & specification. For payment reinforcement including authorized weight for spacer bars, laps, chairs etc shall be measured separately for diameter wise length actually used. Wastages & unauthorized laps shall not be considered for payment. After completion of works Contractor shall take away contractor’s own material/scrap outside the refinery premises. | MT | 300
3 | INITIAL PILE LOAD TESTS
Conducting Initial Pile Load Tests by direct loading/ cyclic loading on piles as per specifications and directions of Engineer- in-Charge
3.1 | Conducting Initial Cyclic Vertical Pile Load Tests by cyclic loading method (by using Concrete blocks only for loading) on piles including equipment, machinery, measuring device, instruments, preparation of pile head, supply & erection of kentledge of suitable magnitude, labour, excavation, back filling, compaction,dewatering etc. all complete as per specifications and directions of Engineer-in-Charge, analyzing the results, making the report and submitting the same in 3 copies (Cost of pile is excluded)
3.1.1 | Diameter of Pile-450 mm | EACH | 1
3.1.2 | Diameter of Pile-600 mm | EACH | 1
3.2 | Conducting Initial Lateral Pile Load Tests by direct loading on piles including equipment, machi- nery, measuring device, instruments, preparation of pile head, labour, excavation, back filling, compac- tion, dewatering etc. all complete as per specifica- tions and directions of Engineer-in-Charge, analyzing the results, making the report and submitting the same in 3 copies (Cost of pile is excluded)
3.2.1 | Diameter of Pile-450 mm | EACH | 1
3.2.2 | Diameter of Pile-600 mm | EACH | 1
3.3 | Conducting Initial Pull Out Load Tests by direct loading on piles including equipment, machinery, measuring device, instruments, preparation of pile head, labour, excavation, back filling, compac- tion, dewatering etc. all complete as per specifica- tions and directions of Engineer-in-Charge, analyzing the results, making the report and submitting the same in 3 copies (Cost of pile is excluded)
3.3.1 | Diameter of Pile-450 mm | EACH | 1
3.3.2 | Diameter of Pile-600 mm | EACH | 1
3.4 | ROUTINE PILE LOAD TESTS
Conducting Routine Pile Load Tests by direct loading on piles as per specifications and directions of Engineer-in-Charge
3.4.1 | Conducting Routine Vertical Pile Load Tests by direct loading (by using Concrete blocks only for loading) on piles including equipment, machinery, measuring device, instruments, preparation of pile head, supply & erection of kentledge of suitable magnitude, labour, excavation, back filling, compac- tion, dewatering etc. all complete as per specifica- tions and directions of Engineer-in-Charge, analyzing the results, making the report and submitting the same in 3 copies (Cost of pile is excluded)
3.4.1.1 | Diameter of Pile-450 mm | EACH | 3
3.4.1.2 | Diameter of Pile-600 mm | EACH | 2
3.4.2 | Conducting Routine Lateral Pile Load Tests by direct loading on piles including equipment, machinery, measuring device, instruments, preparation of pile head, labour, excavation, back filling, compac- tion, dewatering etc. all complete as per specifica- tions and directions of Engineer-in-Charge, analyzing the results, making the report and submitting the same in 3 copies (Cost of pile is excluded)
3.4.2.1 | Diameter of Pile-450 mm | EACH | 3
3.4.2.2 | Diameter of Pile-600 mm | EACH | 2
3.4.3 | Carrying out Pile integrity test on bored cast in-situ concrete piles including equipment, machinery, measuring device, instruments, preparation of pile head as required for testing ,all complete as per procedures/ specifications and directions of Engineer-in-Charge, analyzing the results, making the report and submitting the same in 3 copies (Cost of pile is excluded)
3.4.3.1 | Diameter of Pile-450 mm | EACH | 59
3.4.3.2 | Diameter of Pile-600 mm | EACH | 26
3.4.4 | Carrying out High-strain dynamic test on a single vertical pile as per ASTM D4945-89 with loading equal to 1% to 1.5% of the testing capacity of the pile including necessary arrangements such as equipments, strain transducers, accelometers, Pile Driving Analyser, ram for applying impact load, power supply required for pile testing and pile driver analyzer. The results shall be verified using CAPWAP analysis. ,all complete as per procedures/ specifications and directions of Engineer- in-Charge, analyzing the results, making the report and submitting the same in 3 copies (Cost of pile is excluded)
3.4.4.1 | Diameter of Pile-450 mm | EACH | 6
3.4.4.2 | Diameter of Pile-600 mm | EACH | 3
TOTAL AMOUNT IN FIGURE (IN INR)

## Table 10
PILING AND CIVIL WORKS FOR AVU AND DCU REVAMP, NEW HGU AND OFFSITE UTILITIES AND OFFSITE FACILITIES FOR DR 1.0 EXPANSION PROJECT AT DIGBOI REFINERY OF INDIAN OIL CORPORATION LIMITED
| SCHEDULES OF RATES - CIVIL WORKS TENDER REF. NO:TP/214227C001/T/06 |  |  |  | SP-1 PART B
SL. NO | ITEM DESCRIPTION | UNIT | QTY | UNIT RATE (Rs.) | AMOUNT (Rs.)
1 | AREA DEVELOPMENT JOBS
1.1 | Clearing the area of grass, rank vegetation, wild growth, bushes, trees and plants upto 30 cm girth measured at a height of 1.0M above ground level from road side berms under pipelines and structures, tank farms, drains, yards etc by uprooting/scrapping completely from ground and making good the area, collecting all uprooted vegetation etc., abandoned electrical wires / cables / fittings / fixtures inclusive of loading, transportation with in 6.0 km Lead or part there of with in or outside of owner's battery Limit, unloading and stacking at respective designated places as directed by the Engineer-in- Charge. Job is also inclusive of providing all necessary machinery, equipments, tools & tackles, consumables etc. all complete as per specifications and directions of the Engineer-in-Charge. | SQ.M | 1000
1.2 | Scrubbing & clearing the areas, removal of oily sludge , clearing the site of all objectionable/unserviceable materials by means of manual or mechanical excavation as per directions of Engineer-in-Charge and surface rough-levelled for subsequent works,including loading, transport, unloading and disposal of the unserviceable material at designated areas outside/inside the plant boundary and leveling the same as per the directions of Engineer-in-charge. | SQ.M | 100
2 | SITE GRADING
2.1 | Filling of low lying areas with Moorum/good quality earth supplied by Contractor after excavating the same from Engineer-In- charge/Owner approved borrow areas, loading, transporting the earth to site of work, unloading, laying earth in layers not exceeding 20 cm in depth, breaking clods, watering as required, rolling each layer with minimum ½ tonne roller or other suitable rammers of similar capacity, rolling every 3rd and top-most layer with power roller of minimum 8 tonnes so as to achieve 90% laboratory maximum dry density, dressing of surface etc.. Quoted Price shall be including cost of fillin material along with all royalties payment, all transportation, all loading/unloading arrangements, laying & compaction, de-watering of the ponds/low lying areas wherever required (no separate payment shall be made for de-watering), cutting of Trees/removal bushes/removal of fallen trees etc. from the areas to be filled up, removal of debris/concrete blocks/scrap metallic Items etc. from the areas to be filled up etc. all complete as per the directions of Engineer-in-Charge. (Tree Cutting and Removal of debris/concrete blocks/metallic scrap etc shall be paid separately under the relevant Items of Price-Schedule). | CUM | 100
2.2 | Filling of low lying areas with earth available in other areas within the Refinery premises as per the specific directions of E-i-C including excavation, loading, transporting the earth to site of work, unloading, laying earth in layers not exceeding 20 cm in depth, breaking clods, watering as required, rolling each layer with minimum ½ tonne roller or other suitable rammers of similar capacity, rolling every 3rd and top-most layer with power roller of minimum 8 tonnes so as to achieve 90% laboratory maximum dry density, dressing of surface etc.. Quoted Price shall also include de-watering of the low lying areas wherever required (no separate payment shall be made for de-watering), cutting of Trees/removal bushes/removal of fallen trees etc. from the areas to be filled up, removal of debris/concrete blocks/scrap metallic Items etc. from the areas to be filled up etc. all complete as per th directions of Engineer-in-Charge. (Tree Cutting and Removal of debris/concrete blocks/metallic scrap etc shall be paid separately under the relevant Items of Price-Schedule). | CUM | 200
3 | EXCAVATION IN SOIL
3.1 | Manual Excavation below ground level in normal soils for all kinds of work in foundation including trenches, pavements, manholes, footings, pipelines, cable trenches, barricading,pipe sleepers etc. in ordinary soils including all labour, materials, dressing of sides, leveling, grading and ramming of bottom, pumping & pumping out water accumulated due to rain and/or subsoil waters and including dismantling and providing temporary supports to and / or protecting existing underground lines and facilities, service lines like water pipes, sewerage, instrument / electric cables, etc. complete, including shoring/strutting if required, all materials and labour complete and as directed by Engineer-in-Charge. (Item includes disposal of the surplus earth up to 100 M from the nearest edge of the excavated area)
3.1.1 | From grade level upto 3.0m depth | CUM | 100
3.2 | Machine Excavation below ground level in normal soils for all kinds of work in foundation including trenches, pavements, manholes, footings, pipelines, cable trenches, barricading,pipe sleepers etc. in ordinary soils including all labour, materials, dressing of sides, leveling, grading and ramming of bottom, pumping & pumping out water accumulated due to rain and/or subsoil waters and including dismantling and providing temporary supports to and / or protecting existing underground lines and facilities, service lines like water pipes, sewerage, instrument / electric cables, etc. complete, including shoring/strutting if required, all materials and labour complete and as directed by Engineer-in-Charge. (Item includes disposal of the surplus earth up to 100 M from the nearest edge of the excavated area)
3.2.1 | From grade level upto 1.5m depth | CUM | 300
3.2.2 | From 1.5m depth to 3.0m depth | CUM | 100
4 | BACKFILLLING IN PLINTH/TRENCHES/FOUNDATION PITS ETC.
4.1 | WITH AVAILABLE EXCAVATED EARTH
4.1.1 | Backfilling in section excavation for foundations, plinth, trenches etc to proper grade and level with selected materials from available excavated soil within a lead of 100 meter, including re-excavating the deposited soil excavated earlier, breaking clods, loading, transporting and laying at all depths / heights in layer of 15 cm loose thickness, watering and ramming to proper compaction to achieve 95% laboratory maximum dry density as per IS: 2720 Part-VIII , dressing etc all complete and as per directions of Engineer-in-Charge. | CUM | 190
4.2 | WITH EARTH SUPPPLIED BY CONTRACTOR
4.2.1 | Backfilling in section excavations for foundation, plinth, trenches etc with murrum/good quality earth supplied by Contractor after excavating the same from approved borrow areas, loading, transporting the earth to site of work, unloading, breaking clods and laying at all depths and heights in layers of 20 cm loose thickness, watering and ramming to proper compaction to achieve 95% laboratory maximum dry density as per IS: 2720 Part-VIII, dressing etc. all complete as per directions of Engineer-in-Charge and including certification of used material in compliance with the Soil Recommendations. Price shall be including cost of backfill material along with all royalties. | CUM | 100
4.3 | SAND FILLING
4.3.1 | Supplying and filling clean, coarse sand of approved quality conforming to Zone II & III as per IS 383 under floors, pavements, in foundation and plinth,trenches etc. including cost of sand transportation for all leads, loading & unloading, spreading in layers of 150 mm loose thickness at all depths, watering, ramming, compacting to 90% dry density or as specified in drawing, dressing in slopes horizontally as required and leveling etc. all complete and as per directions of Engineer-in-Charge.( Rate for compacted thickness shall be considered.) | CUM | 100
4.4 | Murrum Filling
4.4.1 | Providing & filling to proper grade and level in plinth, roads & other areas to any thickness with approved quality, clean hard murrum/red stone dust, brought from outside and laid in layers not exceeding 200 mm thickness, including breaking clods, watering, ramming, levelling and consolidation with mechanical rollers/rammers to achieve 90% maximum proctor density dressing, trimming etc, complete as per drawings , specifications & as directed by Engineer in Charge. ( Rate for compacted thickness shall be considered.) | CUM | 100
4.5 | GRAVEL FILLING
4.5.1 | Providing & laying hardcore gravel soling with 90 mm and down graded , in yards, under flooring, trenches, pits, foundations, ramps, road portion etc., including filling recesses by grit, stone chips & approved murrum, watering, dressing, compacting by rolling/ramming etc., complete as per drawings, specifications and as directed by Engineer in Charge. | CUM | 50
5 | DISPOSAL OF SURPLUS EARTH
5 | Carriage of earth by mechanical transport including loading, unloading and stacking all complete as per the direction of the Engineer-in- Charge. (The rates will be applicable to net quantities after deduction of 20 percent for voids) beyond initial lead of 100 M to anywhere at any distance from the site, including re-excavating the deposited soil excavated earlier, transportation, loading, unloading, laying at all depths/heights, stacking, levelling and dressing both the area (viz. from where the earth is carted and where it is deposited) to required levels and slopes complete with all lifts.
5.1 | Inside/Outside Owner’s battery area (beyond 100M and upto 6 KM lead) as per the directions of E-i-C | CUM | 100
5.2 | Inside/Outside Owner’s battery area (beyond 6Km and upto 20 KM lead) as per the directions of E-i-C | CUM | 100
5.3 | Inside/Outside Owner’s battery area (per Km beyond 20Km lead) as per the directions of E-i-C | CUM | 100
6 | ROAD WORKS
6.1 | Earth work in cutting for roads/pavement,culverts etc, in all types of soil,breaking the clods,transporting the earth to disposal area or to the areas to be filled up,levelling and dressing to the required slopes,lead upto 100m as directed and lift upto 2 metres, including clearing and stripping,surface dressing of the existing ground,inequilities of the area to the specified levels and grades,supply of labour,equipment,tools etc., complete as per drawing and the specifications and as per the directions of the Engineer-in-charge. | CUM | 100
6.2 | Supply and laying of stone aggregate of 90mm down to 45mm size for Water Bound Macadum (WBM layer Sub base course for road/paving portion , tough, sound, clean and durable including cost of stone aggregate all royalties, taxes, handling, transportation to site, stacking the same by the side of road with all leads and lifts, spreading and laying to form water bound macadam in layers of each 150 mm compacted thickness to proper grade, camber and level, binding the surface with murrum (0.135-0.15 cum per 10 sqm) including cost of supply of murrum, setting out, dressing to camber consolidating/compacting with 8 to 10T road roller, watering including the required test involved, complete as per drawing, specifications, and directions of Engineer-in-Charge. | CUM | 500
6.3 | Supply and laying of Coarse aggregate of 63mm down to 45mm size for Water Bound Macadum (WBM) layer for base course for road/paving portion , tough, sound, clean and durable including cost of stone aggregate all royalties, taxes, handling, transportation to site, stacking the same by the side of road with all leads and lifts, spreading and laying to form water bound macadam in layers of each 75 mm compacted thickness to proper grade, camber and level, binding the surface with murrum ( 0.07 - 0.09 cum per 10 sqm )including cost of supply of murrum, setting out, dressing to camber consolidating/compacting with 8 to 10T road roller, watering including the required test involved, complete as per drawing, specifications, and directions of Engineer-in- Charge. | CUM | 500
TOTAL AMOUNT IN FIGURE (IN INR)